N4DBA06 Modbus rtu Protocol

Function code

| RS485 address (Station address) (1) | Function (1) | Register address (2) | Read number (2) | CRC16 (2) |
| --- | --- | --- | --- | --- |
|  | 03 Read |  |  |  |
|  | 06 Write |  |  |  |

| Read-only register,Read Function code Is 03 |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- |
| Register address | Register contents | Number of bytes |  | Units | Remarks |
| 0x0000 | (IN1)Vi1 voltage value | 2 |  | 0.01V | such as: Get 0x014A Decimal 330 Voltage = 330 * 0.01 = 3.3V |
| 0x0001 | (IN2)Vi2 voltage value |  |  |  |  |
| 0x0002 | (IN3)Ii Current value | 2 |  | 0.01MA | such as: Get 0X03E8 Decimal 1000 Current=1000 *0.01 = 10MA |
| 0x0003 | (IN4) Digital input | 2 |  | 0X0000 0X0001 | NPN/PNP input 0X0000 No input 0X0001 has input |
| Read / write register; Read function code is 03 ,Write function code is 06 |  |  |  |  |  |
| 0x0007 | (IN1)Vi1 voltage ratio |  | 2 | 0.1% millesimal | This value can be corrected when the Voltage/Current reading deviation is greater than 1%, such as: 1000 means 1:1 1010: 1% increase 990: 1% decrease |
| 0x0008 | (IN2)Vi2 voltage ratio |  |  |  |  |
| 0x0009 | (IN3)Ii Current ratio |  |  |  |  |
| 0x0080 | (OUT1)Vo1 voltage value |  | 2 | 0.01V | such as: input 0X00C8 decimal 200 Out voltage=200*0.01=2.00V |
| 0x0081 | (OUT2)Vo2 voltage value |  |  |  |  |
| 0x0082 | (OUT 3)Io Current value |  | 2 | 0.01MA | such as: input 0X0320 decimal 800 Current=800*0.01=8.00MA |
| 0x0083 | (OUT 4) Digital output |  | 2 | 0X0000 0X0001 | 0X0000 Off 0X0001 On |
| 0x0087 | (OUT 1)Vo1 voltage ratio |  | 2 | 0.1% millesimal | This value can be corrected when the voltage/Current reading deviation is greater than 1%, such as: 1000 means 1:1 1010: 1% increase 990: 1% decrease |
| 0x0088 | (OUT 2)Vo2 voltage ratio |  |  |  |  |
| 0x0089 | (OUT 3)Io Current ratio |  |  |  |  |
| 0x00FE | RS485 address (Station address) |  | 2 |  | Read Address 0XFF Write Address 1-247 |
| 0x00FF | Baud rate |  | 2 |  | 0~4 0:1200 1:2400 2:4800 3:9600（default） 4:19200 5: Factory reset |

Serial baud rate：9600（default），N，8，1

Modbus RTU Communication protocol：

- Read Input channel, 1-2 channel voltage input value, 3 channel current input  value, 4 channel switch input value

Send data

| RS485 address (Station address) (1) | Function (1) | Register address (2) | Read number (2) | CRC16(2) |
| --- | --- | --- | --- | --- |

Returns data

| RS485 address (Station address) (1) | Function (1) | Number of bytes (1) | data (n) | CRC16(2) |
| --- | --- | --- | --- | --- |

RS485 address(Slave ID) : 0x01~0xFE

Function code 0x03

Register address：0x0000-0x0003, 1-2 channel voltage input value, 3 channel current input value, 4 channel switch input value

Read number：0x0001-0x0004

1-2 Channel Voltage(Vi1/Vi2 port):

The return of the Voltage value is two bytes，High-bit in the former and low-bit in the post,convert it to decimal and divided by 100, is the Voltage value, Unit 0.01V; for example:

For example:

Send data(RS485 address is 1)：01 03 00 00 00 01 84 0A

Returns data：01 03 02 00 DB F8 1F

01 RS485 address，03 Function，02 length，F8 1F crc16

00DB is the Voltage value, it is converted to decimal = 219, 219/100=2.19V；

Returns data：01 03 02 01 4B F9 E3

01 4B is the Voltage value, it is converted to decimal =331, 331/100=3.31V；

3 Channel Current(Ii port):

The return of the Current value is two bytes，High-bit in the former and low-bit in the post,convert it to decimal and divided by 100, is the Current value, Unit 0.01MA;

For example:

Send data(RS485 address is 1)：01 03 00 02 00 01 25 CA

Returns data：01 03 02 03 E9 79 3A

01 RS485 address，03 Function，02 length，79 3A crc16

03E7 is the Current value, it is converted to decimal = 999, 999/100=9.99MA；

4-channel Switch input(DiN DiP port):

NPN/PNP input 0X0000 has no input, 0X0001 has input.

Send data(RS485 address is 1) 01 03 00 03 00 01 74 0A

Returns data: 01 03 02 00 00 B8 44 (no input)

Returns data: 01 03 02 00 01 79 84 (with input)

- Read Output channel, 1-2 channel voltage output value, 3 channel current output value, 4 channel switch output value

Send data

| RS485 address (Station address) (1) | Function (1) | Register address (2) | Read number (2) | CRC16(2) |
| --- | --- | --- | --- | --- |

Returns data

| RS485 address (Station address) (1) | Function (1) | Number of bytes (1) | data (n) | CRC16(2) |
| --- | --- | --- | --- | --- |

RS485 address(Slave ID) : 0x01~0xFE

Function code 0x03

Register address：0x0080-0x0083, 1-2 channel voltage output value, 3 channel current output value, 4 channel switch output value

Read number：0x0001-0x0004

1-2 Channel Voltage output(Vo1/Vo2 port):

The return of the Voltage value is two bytes，High-bit in the former and low-bit in the post,convert it to decimal and divided by 100, is the Voltage value, Unit 0.01V; for example:

For example:

Send data(RS485 address is 1)：01 03 00 80 00 01 85 E2

Returns data：01 03 02 00 DB F8 1F

01 RS485 address，03 Function，02 length，F8 1F crc16

00DB is the Voltage value, it is converted to decimal = 219, 219/100=2.19V；

Returns data：01 03 02 01 4B F9 E3

01 4B is the Voltage value, it is converted to decimal =331, 331/100=3.31V；

3-Channel Current output(Io port):

The return of the Current value is two bytes，High-bit in the former and low-bit in the post,convert it to decimal and divided by 100, is the Current value, Unit 0.01MA;

For example:

Send data(RS485 address is 1)：01 03 00 82 00 01 24 22

Returns data：01 03 02 03 E8 B8 FA

01 RS485 address，03 Function，02 length，79 3A crc16

03E8 is the Current value, it is converted to decimal = 1000, 1000/100=10.00MA；

4-channel Switch output(DoN DoP port):

NPN/PNP input 0X0000 has no input, 0X0001 has input.

Send data(RS485 address is 1) 01 03 00 83 00 01 75 E2

Returns data: 01 03 02 00 00 B8 44 (Output Off)

Returns data: 01 03 02 00 01 79 84 (Output On)

- Set output channel, 1-2 channel voltage value output, 3 channel current value output, 4 channel switch output

Send data

| RS485 address (Station address) (1) | Function (1) | Register address (2) | Setting Content (2) | CRC16(2) |
| --- | --- | --- | --- | --- |

Returns data

| RS485 address (Station address) (1) | Function (1) | Register address (2) | Register value (2) | CRC16(2) |
| --- | --- | --- | --- | --- |

RS485 address(Slave ID) : 0x01~0xFE

Function code 0x06

Register address：0x0080-0x0083, 1-2 channel voltage output value, 3 channel current output value, 4 channel switch output value

Setting 1-2 Channel Voltage output(Vo1/Vo2 port):

Setting value: 2 bytes, unit 0.01V. The voltage range set for channel 1 is 0.05-5V, and the voltage range set for channel 2 is 0.10-10V.

For example 1: Let CH1 output 3.3V voltage. Input value 330 and convert it to hexadecimal 014A

Send frame: 01 06 00 00 01 4A 09 AD

Return frame: 01 06 00 00 01 4A 09 AD

For example 2: Let CH2 output 4V voltage. Input value 400 and convert it to hexadecimal 0190

Send frame: 01 06 00 00 01 90 88 36

Return frame: 01 06 00 00 01 90 88 36

Setting 3-Channel Current output(Io port):

Setting value: 2 bytes, unit 0.01MA. The Current range set for channel 3 is 0.5-20MA.

For example 1: Let CH3 output 12MA Current. Input value 1200 and convert it to hexadecimal 04B0

Send frame: 01 06 00 82 04 B0 2A 96

Return frame: 01 06 00 82 04 B0 2A 96

Setting 4-channel Switch output(DoN DoP port):

Send frame: 01 06 00 83 00 01 B9 E2(Output On)

Send frame: 01 06 00 83 00 00 78 22 (Output Off)

- Read Voltage/Current ratio:

The voltage/current ratio value, when the voltage/current reading or output deviation is greater than 1%, it can be corrected by this value, the default is 1000 (03E8)

Send data

| RS485 address (Station address) (1) | Function (1) | Register address (2) | Read number (2) | CRC16(2) |
| --- | --- | --- | --- | --- |

Returns data

| RS485 address (Station address) (1) | Function (1) | Number of bytes (1) | data (n) | CRC16(2) |
| --- | --- | --- | --- | --- |

RS485 address(Slave ID) : 0x01~0xFE

Function code 0x03

Register address 1：0x0007-0x0009; Indicates 1-3 input channel voltage/current ratio value

Read number：0x0001-0x0003

Register address 2：0x0087-0x0089; Indicates 1-3 output channel voltage/current ratio value

Read number：0x0001-0x0003

Return data: 0.1%  millesimal

The voltage/current ratio can be corrected by this value when the voltage/current reading deviation is greater than 1%. The default value is 1000 (3E8).

For example 1:

send data(RS485 address is 1)：01 03 00 07 00 01 35 CB;  07 is input Channel 1

Returns data：01 03 02 03 E8 B8 FA

03E8 is the voltage ratio, which is 1000 in decimal and divided by 1000=1; indicating that channel 1 does not need to modify the voltage value.

For example 2:

send data(RS485 address is 1)：01 03 00 08 00 01 05 C8; 08 is input Channel 2

Returns data：01 03 02 03 DE 38 EC

03DE is the voltage ratio, which is 990 in decimal and divided by 1000=0.99; Indicates that channel 2 reads 0.99 times the actual acquisition value.

- Set voltage/current ratio

When the actual output voltage/current deviation is greater than 1%, it can be corrected by this value, the default is 1000 (03E8)

Send data

| RS485 address (Station address) (1) | Function (1) | Register address (2) | Setting Content (2) | CRC16(2) |
| --- | --- | --- | --- | --- |

Returns data

| RS485 address (Station address) (1) | Function (1) | Register address (2) | Register value (2) | CRC16(2) |
| --- | --- | --- | --- | --- |

RS485 address(Slave ID) : 0x01~0xFE

Function code 0x06

Register address 1：0x0007-0x0009; Indicates 1-3 input channel voltage/current ratio value

Read number：0x0001-0x0003

Register address 2：0x0087-0x0089; Indicates 1-3 output channel voltage/current ratio value

Setting Content：2Bytes

Setting value: 2 bytes, unit 0.1%. When this value is set to 1000 (3E8), the voltage value does not change.

For example 1: The actual voltage of input channel 1 is 5.00V, but the read value is only 4.00V. The ratio deviation is 5/4=1.25, and the correction voltage ratio is changed to 1250, which can correct the input voltage.

Send frame: 01 06 00 07 04 E2 BA 82

Return frame: 01 06 00 07 04 E2 BA 82

The return frame is the same as the send frame. 07 means input channel 1, 04 E2 means correction voltage ratio is 1250

For example 2: The actual voltage of input channel 2 is 4.00V, but the read value is only 5.00V. The ratio deviation is 4/5=0.8, and the correction voltage ratio is changed to 800, which can correct the voltage.

Send frame: 01 06 00 08 03 20 09 20

Return frame: 01 06 00 08 03 20 09 20

The return frame is the same as the send frame. 08 means input channel 2, 03 20 means correction voltage ratio is 800

For example 3: Set the output channel 1 to 5V, but the actual output voltage is 4.9V. Output deviation: 5/4.9=1.020. Input 1020 (0X03FC) to correct the output error

Send frame: 01 06 00 87 03 FC 39 52

Return frame: 01 06 00 87 03 FC 39 52

For example 4: Set the output channel 2 to 4V, but the actual output voltage is 4.1V. Output deviation: 4/4.1=0.975. Input 975 (0X03CF) to correct the output error

Send frame: 01 06 00 88 03 CF 49 44

Return frame: 01 06 00 88 03 CF 49 44

- Read RS485 address

Send data

| RS485 address (Broadcast address) (1) | Function (1) | Register address (2) | Read number (2) | CRC16(2) |
| --- | --- | --- | --- | --- |

Returns data

| RS485 address ( Broadcast address ) (1) | Function (1) | Number of bytes (1) | data (n) | CRC16(2) |
| --- | --- | --- | --- | --- |

Broadcast address 0xff

Function code 0x03

Register address：0x00FE

Read number：0x0001

For example:

send data：FF 03 00 FE 00 01 F0 24

Returns data：FF 03 02 00 01 50 50

FF Broadcast address，03 Function，02 length，01 is the current module RS485 address , 50 50 crc16

Note: When using this command, only one temperature module can be connected to the RS485 bus, more than one will be wrong!

- Write RS485 address

Send data

| RS485 address (Station address) (1) | Function (1) | Register address (2) | Setting Content (2) | CRC16(2) |
| --- | --- | --- | --- | --- |

Returns data

| RS485 address (Station address) (1) | Function (1) | Register address (2) | Register value (2) | CRC16(2) |
| --- | --- | --- | --- | --- |

RS485 address(Slave ID) : 0x01~0xFE

Function code 0x06

Register address：0x00FE

Setting Content：2Bytes(1-247)

For example, The current RS485 address is 1, We need to change the RS485 address to 3:

send data(RS485 address is 1)：01 06 00 FE 00 03 A8 3B

Returns data：01 06 00 FE 00 03 A8 3B

- Read baud rate

Send data

| RS485 address (Station address) (1) | Function (1) | Register address (2) | Read number (2) | CRC16(2) |
| --- | --- | --- | --- | --- |

Returns data

| RS485 address (Station address) (1) | Function (1) | Number of bytes (1) | data (n) | CRC16(2) |
| --- | --- | --- | --- | --- |

RS485 address(Slave ID) : 0x01~0xFE

Function code 0x03

Register address：0x00FF

Read number：0x0001

For example:

send data(RS485 address is 1)：01 03 00 FF 00 01 B4 3A

Returns data：01 03 02 00 03 F8 45

01 RS485 address，03 Function，02 length，F8 45 crc16

03 means the current baud rate is 9600bps

Baud rate corresponds to the number: 0: 1200  1: 2400  2: 4800  3: 9600  4: 19200

- Write baud address

Send data

| RS485 address (Station address) (1) | Function (1) | Register address (2) | Setting Content (2) | CRC16(2) |
| --- | --- | --- | --- | --- |

Returns data

| RS485 address (Station address) (1) | Function (1) | Register address (2) | Register value (2) | CRC16(2) |
| --- | --- | --- | --- | --- |

RS485 address(Slave ID) : 0x01~0xFE

Function code 0x06

Register address：0x00FF

Setting Content：2Bytes(0-4)

For example, Change the baud rate to 4800bps:

send data(RS485 address is 1)：01 06 00 FF 00 02 38 3B

Returns data：01 06 00 FF 00 02 38 3B

Baud rate corresponds to the number: 0: 1200  1: 2400  2: 4800  3: 9600  4: 19200

5: Factory reset

Note: 1 The baud rate will be updated when the module is powered up again!

2 The factory setting can be restored when the baud rate corresponding to the number is 5. For example: 01 06 00 FF 00 05 79 F9

MODBUS commands you can use "Modbus Poll" input, as shown below

（CRC check generated automatically）

You can also use HyperTerminal serial input, as shown below

（Manually add CRC check）