SHA8C01 RS485 SHT30 sensor protocol

Function code

| RS485 address (Station address) (1) | Function (1) | Register address (2) | Read number (2) | CRC16 (2) |
| --- | --- | --- | --- | --- |
|  | 03 Read |  |  |  |
|  | 06 Write |  |  |  |

| Read-only register,Read Function code Is 03 |  |  |  |  |
| --- | --- | --- | --- | --- |
| Register address | Register contents | Number of bytes | Units | Remarks |
| 0x0000 | Temperature value | 2 | 0.1℃ | For example, the data is 255, which is equal to 25.5 ℃ When the data is 0X8000(32768), it indicates no sensor or error |
| 0x0001 | Humidity value | 2 | 0.1%RH | For example, the data is 801, which is equal to 80.1%RH When the data is 0X8000(32768), it indicates no sensor or error |
| Read / write register; Read function code is 03 ,Write function code is 06 |  |  |  |  |
| 0x0002 | RS485 address (Station address) | 2 |  | Read Address 0XFF Write Address 1-247 |
| 0x0003 | Baud rate | 2 |  | 0~4 0:1200 1:2400 2:4800 3:9600（default） 4:19200 5: Factory reset |
| 0x0004 | Temperature correction value | 2 | 0.1℃ | >0 Temperature increase <0 temperature decrease Default : 0 |
| 0x0005 | Humidity correction value | 2 | 0.1%RH | >0 Humidity increase <0 Humidity decrease Default : 0 |
| 0x0006 | Automatic& Humidity upload of temperature | 2 | Second | 0: Query function (default) 1-255: Automatically report, the unit is second. 1: Report every 1 second 2: Report every 2 seconds 10: Report every 10 seconds Maximum interval of 255 seconds |

Serial baud rate：9600（default），N，8，1

Modbus RTU Communication protocol：

- Read temperature

Send data

| RS485 address (Station address) (1) | Function (1) | Register address (2) | Read number (2) | CRC16(2) |
| --- | --- | --- | --- | --- |

Returns data

| RS485 address (Station address) (1) | Function (1) | Number of bytes (1) | data (n) | CRC16(2) |
| --- | --- | --- | --- | --- |

Function code 0x03

Register address：0x0000

Read number：0x0001

The return of the temperature data is two bytes，High-bit in the former and low-bit in the post，convert it to decimal and divided by 10, is the current temperature value；The highest bit 1 indicates a negative value， this value directly subtracting  65536，is the current temperature value.

For example:

send data(RS485 address is 1)：01 03 00 00 00 01 84 0A

Returns data：01 03 02 00 DB F8 1F

01 RS485 address，03 Function，02 length，F8 1F crc16

00DB is the temperature value, the highest bit is 0, so the temperature is positive, it is converted to decimal = 219, 219/10=21.9 is the current temperature value；

Returns data：01 03 02 FF 90 F2 3F

FF90 is the temperature value, the highest bit is 1, so the temperature is negative, it is converted to decimal = 65424, (65424-65536)/10=-11.2 is the current temperature value

- Read Humidity value

Send data

| RS485 address (Station address) (1) | Function (1) | Register address (2) | Read number (2) | CRC16(2) |
| --- | --- | --- | --- | --- |

Returns data

| RS485 address (Station address) (1) | Function (1) | Number of bytes (1) | data (n) | CRC16(2) |
| --- | --- | --- | --- | --- |

Function code 0x03

Register address：0x0001

Read number：0x0002

The return of the Humidity value data is two bytes，High-bit in the former and low-bit in the post，convert it to decimal and divided by 10, is the Humidity value ；

For example:

send data(RS485 address is 1)：01 03 00 01 00 01 D5 CA

Returns data：01 03 02 03 3A 38 A7

01 RS485 address，03 Function，02 length，38 A7 crc16

033A is the Humidity value, it is converted to decimal = 826, 826/10=82.6 is the Humidity value；

- Read RS485 address

Send data

| RS485 address (Broadcast address) (1) | Function (1) | Register address (2) | Read number (2) | CRC16(2) |
| --- | --- | --- | --- | --- |

Returns data

| RS485 address ( Broadcast address ) (1) | Function (1) | Number of bytes (1) | data (n) | CRC16(2) |
| --- | --- | --- | --- | --- |

Broadcast address 0xff

Function code 0x03

Register address：0x0002

Read number：0x0001

For example:

send data：FF 03 00 02 00 01 30 14

Returns data：FF 03 02 00 01 50 50

FF Broadcast address，03 Function，02 length，01 is the current module RS485 address , 50 50 crc16

Note: When using this command, only one temperature module can be connected to the RS485 bus, more than one will be wrong!

- Write RS485 address

Send data

| RS485 address (Station address) (1) | Function (1) | Register address (2) | Setting Content (2) | CRC16(2) |
| --- | --- | --- | --- | --- |

Returns data

| RS485 address (Station address) (1) | Function (1) | Register address (2) | Register value (2) | CRC16(2) |
| --- | --- | --- | --- | --- |

Function code 0x06

Register address：0x0002

Setting Content：2Bytes(1-247)

For example, The current RS485 address is 1, We need to change the RS485 address to 3:

send data(RS485 address is 1)：01 06 00 02 00 03 68 0B

Returns data：01 06 00 02 00 03 68 0B

- Read baud rate

Send data

| RS485 address (Station address) (1) | Function (1) | Register address (2) | Read number (2) | CRC16(2) |
| --- | --- | --- | --- | --- |

Returns data

| RS485 address (Station address) (1) | Function (1) | Number of bytes (1) | data (n) | CRC16(2) |
| --- | --- | --- | --- | --- |

Function code 0x03

Register address：0x0003

Read number：0x0001

For example:

send data(RS485 address is 1)：01 03 00 03 00 01 74 0A

Returns data：01 03 02 00 03 F8 45

01 RS485 address，03 Function，02 length，38 F1 crc16

03 means the current baud rate is 9600bps

Baud rate corresponds to the number: 0: 1200  1: 2400  2: 4800  3: 9600  4: 19200

- Write baud rate

Send data

| Slave ID(Device Address) (1) | Function (1) | Register address (2) | Setting Content (2) | CRC16(2) |
| --- | --- | --- | --- | --- |

Returns data

| Slave ID(Device Address) (1) | Function (1) | Register address (2) | Register value (2) | CRC16(2) |
| --- | --- | --- | --- | --- |

Function code 0x06

Slave ID : 0x01~0xFE

Register address：0x0003

Setting Content：2Bytes(0-4)

For example, Change the baud rate to 4800bps:

send data(Slave ID is 1)：01 06 00 03 00 02 F8 0B

Returns data：01 06 00 03 00 02 F8 0B

Baud rate corresponds to the number: 0: 1200  1: 2400  2: 4800  3: 9600  4: 19200

5: Factory reset

Note: 1 The baud rate will be updated when the module is powered up again!

2 The factory setting can be restored when the baud rate corresponding to the number is 5. For example: 01 06 00 03 00 05 B9 C9

- Set the temperature correction value

If the temperature of the module deviates from the actual temperature, it can be corrected with this value. >0 temperature increases, <0 temperature decreases.

Send data

| RS485 address (Station address) (1) | Function (1) | Register address (2) | Setting Content (2) | CRC16(2) |
| --- | --- | --- | --- | --- |

Returns data

| RS485 address (Station address) (1) | Function (1) | Register address (2) | Register value (2) | CRC16(2) |
| --- | --- | --- | --- | --- |

Function code 0x06

Slave ID : 0x01~0xFE

Register address：0x0004

Setting Content：2Bytes

The highest digit indicates a positive or negative sign, 0 indicates positive, and 1 indicates negative, and the unit is 0.1 °C. When the highest bit is 1, it indicates a negative value. In this case, you need to add 1 to this value. You can also subtract 65536 from the value, which is the current temperature value. Prohibit the correction value to set the register to "0X0000"

For example 1: offset value is set to 2.0 °C

Send frame: 01 06 00 04 00 14 C8 04

Return frame: 01 06 00 04 00 14 C8 04 The return frame is the same as the send frame.

For example 2: the offset value is set to -3.0 ° C, 65536-30 = 65506 =0XFFE2

Send frame: 01 06 00 04 FF E2 09 B2

Return frame: 01 06 00 04 FF E2 09 B2 The return frame is the same as the send frame.

For example 3: Prohibit the correction value and set the register to "0X0000"

Send frame: 01 06 00 04 00 00 C8 0B

Return frame: 01 06 00 04 00 00 C8 0B The return frame is the same as the send frame.

- Set the Humidity correction value

If the Humidity of the module deviates from the actual Humidity, it can be corrected with this value. >0 Humidity increases, <0 Humidity decreases.

Send data

| RS485 address (Station address) (1) | Function (1) | Register address (2) | Setting Content (2) | CRC16(2) |
| --- | --- | --- | --- | --- |

Returns data

| RS485 address (Station address) (1) | Function (1) | Register address (2) | Register value (2) | CRC16(2) |
| --- | --- | --- | --- | --- |

Function code 0x06

Slave ID : 0x01~0xFE

Register address：0x0004

Setting Content：2Bytes

The highest digit indicates a positive or negative sign, 0 indicates positive, and 1 indicates negative, and the unit is 0.1 %RH. When the highest bit is 1, it indicates a negative value. In this case, you need to add 1 to this value. You can also subtract 65536 from the value, which is the current Humidity value. Prohibit the correction value to set the register to "0X0000"

For example 1: offset value is set to 2.0 %RH

Send frame: 01 06 00 05 00 14 99 C4

Return frame: 01 06 00 05 00 14 99 C4 The return frame is the same as the send frame.

For example 2: the offset value is set to -3.0 %RH, 65536-30 = 65506 =0XFFE2

Send frame: 01 06 00 05 FF E2 58 72

Return frame: 01 06 00 05 FF E2 58 72 The return frame is the same as the send frame.

For example 3: Prohibit the correction value and set the register to "0X0000"

Send frame: 01 06 00 05 00 00 99 CB

Return frame: 01 06 00 05 00 00 99 CB The return frame is the same as the send frame.

- Read temperature& Humidity automatic reporting function

Send data

| RS485 address (Station address) (1) | Function (1) | Register address (2) | Read number (2) | CRC16(2) |
| --- | --- | --- | --- | --- |

Returns data

| RS485 address (Station address) (1) | Function (1) | Number of bytes (1) | data (n) | CRC16(2) |
| --- | --- | --- | --- | --- |

Function code 0x03

Register address：0x0006

Slave ID : 0x01~0xFE

Read number：0x0001

For example:

send data(RS485 address is 1)：01 03 00 06 00 01 64 0B

Returns data：01 03 02 00 00 B8 44

01 RS485 address，03 Function，02 length，00 means query function ,

B8 44 crc16

- Set temperature automatic reporting function

Send data

| RS485 address (Station address) (1) | Function (1) | Register address (2) | Setting Content (2) | CRC16(2) |
| --- | --- | --- | --- | --- |

Returns data

| RS485 address (Station address) (1) | Function (1) | Register address (2) | Register value (2) | CRC16(2) |
| --- | --- | --- | --- | --- |

Function code 0x06

Register address：0x0006

Setting Content：1Bytes

For example : For example, the current query function should be changed to automatic reporting:

Automatically report in 1 second, send frame (address is 1) 01 06 00 06 00 01 A8 0B

Automatically report in 2 second, send frame (address is 1) 01 06 00 06 00 02 E8 0A

Automatically report in 3 second, send frame (address is 1) 01 06 00 06 00 03 29 CA

Automatically report in 4 second, send frame (address is 1) 01 06 00 06 00 04 68 08

Automatically report in 5 second, send frame (address is 1) 01 06 00 06 00 05 A9 C8

Automatically report in 10 second, send frame (address is 1) 01 06 00 06 00 0A E9 CC

Disable reporting function: send frame (address is 1) 01 06 00 06 00 00 69 CB

For example: set to 1 second to automatically report, and automatically send temperature and humidity data every second;

Example: 01 03 04 01 2F 03 33 8A E3

01 address code, 03 function code, 04 length, 8A E3 crc16

012F is the temperature value, the highest digit is 0, so the temperature is positive, convert it to decimal = 303 divided by 10: 30.3 degrees;

0333 is the humidity value, convert it to decimal = 819 and divide it by 10: the humidity value before 81.9;

MODBUS commands you can use "Modbus Poll" input, The value of 7 registers can be read as shown below（CRC check generated automatically）

You can also use HyperTerminal serial input, as shown below

（Manually add CRC check）